## Slide 1
1926 Construction
Focus Four
Electrical Hazards

## Slide 2: ELECTRICAL HAZARDS Focus Four
Objectives
By the end of the session students will be able to:
List common causes of electrical injuries.
List ways to reduce exposure to electrical hazards.
Describe what to do if a co-worker gets shocked.

## Slide 3: ELECTRICAL HAZARDS Focus Four
Electricity Can Kill You
Contact with live circuits in electrical panels or exposed wiring
Contact with overhead power lines
Improperly maintained cords and power tools
Arc-Flash
Notes: Average workers who work with what is called “household current”, 120-volt, 15 to 20-amp single phase power are electrocuted and die each year.
Some common electrical hazards are listed.

## Slide 4: ELECTRICAL HAZARDS Focus Four
Effects of Electricity on People
Harm is related to amps, duration of contact, and the path by which current passes through the body.
Notes: This slide shows the affect that electricity has on the human body. The chart shows different current (Amp) levels and the effects of contact.
The three things that contribute to injury from electrical shock are the level of current, duration of contact, and the path the current takes through the body.

## Slide 5: Electrocution deaths caused by electric parts in construction, by primary source, 2011-2015 total
ELECTRICAL HAZARDS Focus Four
Chart: 
| Power lines, transformers, convertors | Electrical wiring—building | Switchboards, switches, fuses | Power cords, electrical cords, extension cords | Other
 | 0.38624 | 0.37037 | 0.13228 | 0.031746 | 0.079365
Notes: Source: CPWR
https://www.cpwr.com/research/data-center/the-construction-chart-book/chart-book-6th-edition-fatal-and-nonfatal-injuries-fatalities-from-contact-with-electricity-in-construction-2/
Of the 189 deaths caused by electric parts in construction from 2011 to 2015, power-lines, transformers, and converters, as well as electrical building wiring were the two major sources, responsible for 39% and 37% of such deaths, respectively.

## Slide 6: ELECTRICAL HAZARDS Focus Four
Since 2012, 22% of Elevator Constructor deaths have been Electricity-related.
Elevator Industry-Related Electrical Hazards

## Slide 7: ELECTRICAL HAZARDS Focus Four
Working Around Power Lines
Overhead power lines carry extremely high voltage.
Contact can cause electrocution, burns, and falls from elevations.
Equipment contact with power lines can cause explosions and fire.
Notes: Before outdoor work begins, your employer should call utility companies to locate underground power lines and to turn off or insulate (if possible) any overhead power lines near your work.
If overhead lines cannot be turned off or insulated, there should be warning cones or other barriers to prevent equipment from getting too close. Unless you know for sure that an overhead power line is turned off, stay at least 10 feet away – more than 10 feet if the line is over 50,000 volts.

## Slide 8: ELECTRICAL HAZARDS Focus Four
Overhead lines are typically not insulated. The covering on high power lines is generally a weather protection, not insulation.
Power Line Facts
In cranes or backhoe-type equipment, operators are normally safe when equipment accidentally touches a power line… if they stay inside their equipment.
Workers on the ground who come in contact with power lines are 8 times more likely to be killed than workers inside equipment or vehicles.
Notes: A real danger is when the body of the crane or backhoe is energized and a person standing on the ground touches a metal part of the equipment. The worker will become part of the circuit and will likely be electrocuted.
The case study the class will discuss on slide 16 involves this kind of fatality.

## Slide 9: ELECTRICAL HAZARDS Focus Four
Working Safely Around Overhead Power Lines
Locate overhead lines before starting the job
Keep at least 10 feet away from 50 kV or less
Always assume that lines are energized
De-energize and ground power lines when working within 10’
Notes: Illustration of the 10ft danger zone.
1926.1408 Table A establishes minimum clearance distance.

## Slide 10: ELECTRICAL HAZARDS Focus Four
If Equipment Contacts a Power Line the Ground May Become Energized!
Electricity dissipates with the resistance of the ground
As potential drops, fields develop around the electrified machine
If you step across a line of unequal potential, you could be electrocuted
Notes: Energy fields may be generated around the grounded object. If a person steps across two different levels of voltage or touches an object at a different level, electricity will pass through the body.

## Slide 11: ELECTRICAL HAZARDS Focus Four
What to Do If Equipment Contacts Overhead Power Lines
If you are not on or in the equipment… stay away from it!!
Do not touch the machine or outriggers
If you are operating it, stay in it until power is shut off
If you must get out, jump with your feet together
Hop or shuffle away
Notes: Often, the power going to ground after contact will blow the utility breaker and the power will be off. However, some utilities will automatically reset and the line will be reenergized. If there is no reason to get out of the equipment cab the best recommendation is to notify the utility and sit tight until the operator is sure the power is off.
The current flow can cause a fire. The engine can catch on fire and or the tires can also catch on fire. In this situation the operator will have to exit.

## Slide 12: ELECTRICAL HAZARDS Focus Four
Elevator Industry-Related Electrical Hazards
Even though as an Elevator Constructor you may not be operating this equipment outside of the building, you should be aware of the potential for these accidents to happen.
Remember, simply being in the vicinity of a piece of equipment that becomes energized could cause you injury.
A crane that becomes energized from overhead power lines
could energize the load or any crane attachments.

## Slide 13: ELECTRICAL HAZARDS Focus Four
Working Around Temporary Electrical Circuits on Job Sites
GFCIs
Assured equipment grounding
Extension cords
Electrical panel boxes
We will discuss four specific topics regarding temporary construction wiring:

## Slide 14: ELECTRICAL HAZARDS Focus Four
Ground Fault Circuit Interrupters (GFCI)
Protect workers from shock by limiting duration of electrical shock*
Monitor the difference in current between the hot and neutral wires
Trip between 4-6 mA and shut off electricity in 1/40th of a second
Must be used on all 120 volt, single-phase 15 and 20 amp receptacles
Notes: The federal government says that GFCIs can eliminate over two-thirds of all electrocutions.
OSHA says each 120-volt, 15 or 20 amp outlet that is not part of permanent building wiring must have a ground fault circuit interrupter (GFCI). [1926.404(b)(1)(ii)]
The only exception is if the site has a written Assured Equipment Grounding Conductor Program (AEGCP). The next slide explains the Assured Grounding Conductor program (see factsheet in this binder). [1926.404(b)(1)(iii)]

## Slide 15: ELECTRICAL HAZARDS Focus Four
Assured Equipment Grounding Program
Required If GFCIs are not used
Inspection ensures your protection
The most common color-coding system uses these colors to indicate inspection has been done
Fall
Summer
Spring
Winter
Notes: Employers must provide GFCIs or put in place the Assured Equipment Grounding Program.
Advise students that testing should be done regardless of whether GFCIs are in use.

## Slide 16: ELECTRICAL HAZARDS Focus Four
Extension Cords
Inspect your cords
Ensure the insulation isn’t damaged
Confirm the grounding prong is intact
Don’t run cords through windows, doors, or holes in a wall without protection
Should be labeled and must be 3-wire type designed for hard or extra hard use
Notes: The orange flexible cord is damaged. This could have occurred from door or window edges, by staples and fastenings, by abrasion from adjacent materials, or simply by aging.
If the electrical conductors become exposed, there is a danger of shocks, burns, or fire.
29 CFR 1926.405(g)(1)(iii)(C) states that it is prohibited to run a cord through doorways, windows, or similar openings.
The only exception is 29 CFR 1926.405(a)(2)(ii)(I). This citation allows cords to be run through openings as long as they are protected.
The OSHA construction standard requires flexible cords to be rated for hard or extra-hard usage. These ratings are derived from the National Electrical Code, and cords are required to be indelibly marked approximately every foot along the length of the cord. Examples of these codes are: S, ST, SO, and STO for hard service, and SJ, SJO, SJT, and SJTO for junior hard service.

## Slide 17: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?

## Slide 18: ELECTRICAL HAZARDS Focus Four
Yes

## Slide 19: Recognize Any Hazard(s)?

## Slide 20: Yes
Flexible cords and cables may pass through doorways or other pinch points, if protection is provided to avoid damage
Is this foam really adequate to
protect this cord?
Notes: A piece of foam insulation is not adequate protection for power cords. The door must be blocked using something solid that prevents the door making contact with the cord.
The provision allowing cords to go through doors and openings as long as the cord is protected is: 29 CFR 1926.405(a)(2)(ii)(I)
If the cord is not protected it is prohibited to run a cord through doorways, windows, or similar openings in 29 CFR 1926.405(g)(1)(iii)(C)

## Slide 21: ELECTRICAL HAZARDS Focus Four
Always provide proper strain relief when hanging any type of cord.
Notes: [1926.405(g)(2)(iv)]

## Slide 22: ELECTRICAL HAZARDS Focus Four
Temporary Wiring Hazards:
Wiring like this must be protected in closed junction boxes.
Exposed wires are an electric shock hazard.
Even when properly wired, job site conditions change, and temporary electrical components can become unsafe from rough treatment over time
Notes: This wiring cannot be left exposed.
Stress that all electrical wire must be properly protected inside electrical boxes.
Construction sites are subject to daily changes from weather, changes in systems, and the rough process of building.

## Slide 23: ELECTRICAL HAZARDS Focus Four
Workers could be exposed to live wires around the perimeter of this box
Energized electrical panels must be completely covered with a hard cover (original intended equipment)
Do not use cardboard as a cover
Notes: This is not considered protected.
Stress the need for all live circuitry to be covered or protected.
Electricians cannot leave panel boxes unattended with the covers off.

## Slide 24: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?

## Slide 25: ELECTRICAL HAZARDS Focus Four
YES
Notes: The green ground wire is connected from the receptacle to the box but the box itself is not grounded to anything.

## Slide 26: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?

## Slide 27: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?
These cords are improperly wired directly to the electrical circuit
Not protected by a GFCI
Two-wire cords are not grounded and not rated for hard or extra-hard service
Notes: How To Avoid Cord Hazards
Use factory-assembled cord sets.
Use only extension cords that are 3-wire type.
Use only extension cords that are marked with a designation code for hard or extra-hard usage.
Remove cords from receptacles by pulling on the plugs, not the cords.
Inspect cords on-site. Any cords found not to be marked for hard or extra-hard use, or which have been modified, should be taken out of service immediately.
Keep all cords away from water, heat, oil, and sharp edges.
https://www.osha.gov/electrical/hazards

## Slide 28: ELECTRICAL HAZARDS Focus Four
Power Tool Safety
Keep cords away from water, heat, oil, and sharp edges
Disconnect tools when not in use, before servicing, and when changing accessories such as blades
Never yank the cord to disconnect it from the receptacle.
Never carry a tool by the cord
ALL power tools must be double-insulated or have a 3- wire cord
Notes: How To Avoid Cord Hazards
Use factory-assembled cord sets.
Use only extension cords that are 3-wire type.
Use only extension cords that are marked with a designation code for hard or extra-hard usage.
Remove cords from receptacles by pulling on the plugs, not the cords.
Inspect cords on-site. Any cords found not to be marked for hard or extra-hard use, or which have been modified, should be taken out of service immediately.
Keep all cords away from water, heat, oil, and sharp edges.

## Slide 29: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?

## Slide 30: ELECTRICAL HAZARDS Focus Four
YES

## Slide 31: ELECTRICAL HAZARDS Focus Four
What Should You Do If Someone Does Gets Shocked?
If possible, turn off the power.
Have someone call 911 and get an AED if available
Do not touch the worker in contact with live electric current. You could get shocked and become a second victim
Use nonconductive material to remove the person from the power source (a board, rope, etc.)
When the scene is safe, start CPR or other first aid.
Notes: Non conductive material: like a dry wooden pole. This does not apply to high voltage lines.
A branch from a tree or a new 2X4 may have enough water in it to conduct electricity.
OSHA says there must be people trained in first aid on the site.
An AED (defibrillator) can help if a severe shock causes certain heart problems. It can save lives!
The American heart Association provides First Aid/CPR/AED courses. Please consider taking one.

## Slide 32: ELECTRICAL HAZARDS Focus Four
One employee was climbing a metal ladder to hand an electric drill to the journeyman installer on a scaffold about five feet above him. When the victim reached the third rung from the bottom of the ladder, he received an electric shock that killed him. The investigation revealed that the extension cord had a missing grounding prong and that a conductor on the green grounding wire was making intermittent contact with the energizing black wire thereby energizing the entire length of the grounding wire and the drill's frame. The drill was not double insulated.
INSPECTION RESULTS: As a result of its investigation, OSHA issued citations for violations of construction standards.
Accident Report:

## Slide 33: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
§ 1926.416 General requirements.
(a) Protection of employees—(1) No employer shall permit an employee to work in such proximity to any part of an electric power circuit that the employee could contact the electric power circuit in the course of work, unless the employee is protected against electric shock by deenergizing the circuit and grounding it or by guarding it effectively by insulation or other means.

## Slide 34: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
If troubleshooting or testing must be performed with the power on, refer to your company’s live electrical safe work practices policy.
Once the problem is identified, shut the power off, then lock out and tag out the conveyance before performing the repair.
When work is performed on a conveyance requiring employees to place any part of their body within range of energized circuits, pinch points, points of operation, rotating or oscillating parts or where operation is not required, the conveyance must be completely de-energized, locked out and tagged. If operation is required, proper protective guards or insulation must be in place.
Notes: §1926.960 — Working on or near exposed energized parts
(a) Application. This section applies to work on exposed live parts, or near enough to them to expose the employee to any hazard they present. [1926.960(a)]
(b) General. [1926.960(b)]
(1) Qualified employees only. [1926.960(b)(1)]
(i) Only qualified employees may work on or with exposed energized lines or parts of equipment. [1926.960(b)(1)(i)]
(ii) Only qualified employees may work in areas containing unguarded, uninsulated energized lines or parts of equipment operating at 50 volts or more. [1926.960(b)(1)(ii)]
(2) Treat as energized. Electric lines and equipment shall be considered and treated as energized unless they have been deenergized in accordance with §1926.961. [1926.960(b)(2)]

## Slide 35: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
Lockout/Tagout
A lockout/tagout procedure is required after equipment is de-energized to make sure that it is not accidentally re-energized.
Your employer determines the lockout/tagout procedure and must provide training on that procedure. Your employer provides the locks and tags. As an employee, you are responsible for installing these devices as instructed.
Lockout/tagout equipment needs to be unique and readily identifiable as lockout/tagout devices. These locks and tags are not to be used for any other purpose.

## Slide 36: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
For lockout/tagout procedures, only key or combination locks may be used. All lockout devices must list the name of the person who installed it, which is normally written on the tag. This individual is responsible for holding on to the key or combination until the lock is removed.
Tags used along with a lockout device need to contain a statement prohibiting unauthorized operation of the disconnecting means or unauthorized removal of the device.
Tags need to be made of a material that cannot be easily torn off and must be securely attached, following your company’s guidelines. Do not reuse a tag filled out for another task.

## Slide 37: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
LOTO equipment must be identifiable as LOTO specific
LOTO for power tools or equipment with a plug
LOTO for circuit breakers
LOTO for multiple locks

## Slide 38: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
Following is a general step by step process for performing LOTO. Always follow your company's policy and procedures.
Lockout/Tagout (LOTO) Sequence of Steps
1. Gain control of the conveyance and ensure that it is secured from public access. Make sure all necessary PPE and diagnostic hardware is readily available prior to commencing energy shut down.
2. Identify and locate the specific circuit or conveyance and corresponding disconnect you intend to de-energize. Stand to the side and face away while switching off the disconnect.

## Slide 39: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
Lockout/Tagout (LOTO) Sequence of Steps cont.
3. Place the appropriate lock to isolate the equipment. NOTE: If more than one employee is working on the equipment that is locked out, each employee shall place his/her personal lock on the disconnect.
4. Place a “Danger: Do Not Operate” tag with the following four items: company name, employee name, date and a contact number.

## Slide 40: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
Lockout/Tagout (LOTO) Sequence of Steps cont.
5. Identify a known LIVE voltage source, and test the functionality of the multimeter or non-contact voltage detector against this source.

## Slide 41: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
Lockout/Tagout (LOTO) Sequence of Steps cont.
6. Test and verify that the voltage has been disconnected (DEAD) with a non-contact voltage detector or a multimeter. Check each leg to ground. For ungrounded or above-ground systems, check leg to leg to complete verification of absence of energy.
NOTE: If only de-energizing the mainline, be aware that the controller may still have live 110/120-volt circuit for cab lighting and fan. Also verify that voltage has been dissipated from capacitors and AC Drive units.

## Slide 42: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
Lockout/Tagout (LOTO) Sequence of Steps cont.
7. Reverify that the functionality of the multimeter or non-contact voltage detector worked properly before and after the measurement. Check against a known LIVE voltage source.
8. Ensure that all potentially hazardous stored energy is relieved, disconnected, restrained, and otherwise rendered safe. Hydraulic elevator units must be landed on buffers, pipe stands, or have rail blocks installed when working on the pressurized system. Mechanical safeguarding of escalators and moving walks shall be put in place to protect from stored energy.

## Slide 43: ELECTRICAL HAZARDS Focus Four
Lockout/Tagout
Lockout/Tagout (LOTO) Sequence of Steps cont.
9. Perform work.
10. Re-energize the conveyance following these steps:
  Replace all guards and remove all tools
  Recheck to ensure control of the conveyance and that is secure from public access
  The employee(s) who applied personal locks shall remove their own lock and tag
  Stand to the side and face away, announce “power going on” when powering the disconnect on
  Check that the conveyance has been properly returned to service
  Make sure all workers are safe and accounted for before equipment and circuits are unlocked and turned back on

## Slide 44: ELECTRICAL HAZARDS Focus Four
Arc Flash
What is an Arc Flash?
An arc flash is a sudden, unexpected discharge of electricity that travels through the air between conductors, or from conductor to ground.
This short circuit releases enormous amounts of energy as light and heat.
The results can be devastating. When an unprotected person is nearby, serious injury and even death can occur.

## Slide 45: ELECTRICAL HAZARDS Focus Four
Arc Blast
What is an Arc Blast?
An arc flash almost always results in an arc blast. An arc blast is the high-pressure explosion caused by a sudden arc fault.
Although an arc flash and an arc blast are two distinct parts of a split-second phenomenon, for the duration of this course we’ll usually refer to them together as an arc flash.

## Slide 46: ELECTRICAL HAZARDS Focus Four
Common Causes of Arc Flash
Common causes include:
Dust
Dropping tools
Accidental touching
Condensation
Material failure
Corrosion
Faulty installation
Wiring errors

## Slide 47: ELECTRICAL HAZARDS Focus Four
Results of an Arc Flash
Results of an Arc Flash:
It takes little imagination to predict how much damage an arc flash can do to you or one of your coworkers. The blast radius can exceed ten feet, injuring everyone in its path. The dangers associated with arc flash are:
Thermal Energy
The sun burns at about 10,000 degrees Fahrenheit. By comparison, an arc flash can generate temperatures as high as 35,000 degrees Fahrenheit. At this extraordinarily high temperature, all known materials vaporize instantly, causing them to rapidly expand. The resulting fire can spread rapidly, resulting in catastrophic burns, smoke inhalation or death
Ultraviolet Energy
The arc’s high intensity flash can cause blindness
Acoustical Energy
The sound can reach 140 decibels, causing permanent hearing loss

## Slide 48: ELECTRICAL HAZARDS Focus Four
Results of an Arc Flash cont.
Pressure Wave
The pressure wave caused by the blast can hit a worker’s chest with a force greater than 2,000 pounds per square foot causing internal injuries, collapsed lungs, broken bones and/or falls.
Debris
In the explosion that results from the rapid expansion of these materials, droplets of molten metal spray with such force that they can penetrate the body like shrapnel. Depending on the force of the blast this debris can be ejected a great distance from the source of the blast, injuring nearby workers.

## Slide 49: ELECTRICAL HAZARDS Focus Four
Arc Flash Injuries
Due to the violent nature of an arc flash, injuries are serious. This type of accident kills hundreds of workers every year.
If a person survives an arc flash, extended medical care is often required. Burn recovery is an incredibly painful process.
It’s not uncommon for an arc flash survivor to never regain their past quality of life.

## Slide 50: ELECTRICAL HAZARDS Focus Four
Arc Flash Prevention
Preventing an arc flash incident starts by following up-to-date safe work practices and procedures. The National Fire Protection Association, or NFPA, publishes current safe work practices that will enable you to recognize and avoid arc flash hazards.
Almost all arc flash accidents happen when workers are untrained or ignore safe work practices.
Never work on an electrical task without being properly
qualified for the work being performed.

## Slide 51: ELECTRICAL HAZARDS Focus Four
Arc Flash Standards
Who sets the standards for arc flash safety?
National Fire Protection Association (NFPA)
National Electrical Safety Code (NESC)
National Electrical Code (NEC)
Occupational Safety and Health Administration (OSHA)

## Slide 52: ELECTRICAL HAZARDS Focus Four
Electrically Safe Working Conditions
What are Electrically Safe Working Conditions?
In general, OSHA determines what is required to create electrically safe working conditions, and NFPA 70E describes how to create electrically safe working conditions.
An electrically safe working condition is defined as a state in which an electrical conductor or circuit part has been disconnected from energized parts, locked and tagged in accordance with established standards, tested to ensure the absence of voltage, and grounded if determined necessary.
In a few words:
work de-energized whenever possible.

## Slide 53: ELECTRICAL HAZARDS Focus Four
Responsibilities
Responsibility for Safe Conditions
Both employers and employees have responsibilities for creating electrically safe working conditions
Employers need to establish the safety-related work practices and train workers.
Employees need to implement the safe work practices
It’s vital that you follow safe work practices. The consequences are too extreme to take a chance

## Slide 54: ELECTRICAL HAZARDS Focus Four
Elevator Industry-Related Electrical Hazards
To eliminate the risk for contact with live electrical wiring, hoistway and car connections should be made before controller connections.

## Slide 55: ELECTRICAL HAZARDS Focus Four
Elevator Industry-Related Electrical Hazards
Car top junction boxes, car operating panels, and controllers should be neat and organized when construction wiring is complete.
Notes: Neat wiring will easily show a stray wire that has come out from a terminal.

## Slide 56: ELECTRICAL HAZARDS Focus Four
Elevator Industry-Related Electrical Hazards
Do you see the hazard here?
There is no protection for the wires being brought into this box. It’s just a matter of time until vibration wears away the wires insulation and the live conductor contacts the metal.
Protection must be provided any time cables or wires are brought into a box or controller. This can be accomplished with a bushing or other edge protection.

## Slide 57: ELECTRICAL HAZARDS Focus Four
Elevator Industry-Related Electrical Hazards
Control cabinet doors should be closed any time work is not being done. This will eliminate accidental contact with any live components. The controller may be located inside the hoistway and only accessible from the car top. Whenever possible, perform LOTO procedures before doing any work inside the control panel. Always follow your company’s LOTO and live work processes.

## Slide 58: ELECTRICAL HAZARDS Focus Four
Elevator Industry-Related Electrical Hazards
Escalators and moving walks present some challenges for wiring and LOTO. Tight quarters require you to be in close proximity to caught in/between and electrical hazards. Always perform LOTO procedures and secure the unit from unintended movement before putting yourself in a position for potential injury.

## Slide 59: ELECTRICAL HAZARDS Focus Four
Hazard Identification
Can you identify the hazards
in these next slides?
Look at the picture and
identify the hazards.
Have a discussion about
possible solutions.

## Slide 60: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?

## Slide 61: ELECTRICAL HAZARDS Focus Four
Yes
Notes: No employer shall permit a worker to work in such proximity to any part of an electric power circuit that the worker could contact the electric power circuit in the course of work

## Slide 62: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?

## Slide 63: ELECTRICAL HAZARDS Focus Four
Yes
Crossing electrical line must be supported, protected, or removed to safeguard workers

## Slide 64: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?

## Slide 65: ELECTRICAL HAZARDS Focus Four
Yes
Scaffold was erected 4 ½ feet from 7.2 kV power lines

## Slide 66: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?

## Slide 67: ELECTRICAL HAZARDS Focus Four
Yes
Continuous path to ground not maintained; multiple cords used for fixed equipment
Notes: The extension cord appears to be an 18-gauge light duty cord supplying power.

## Slide 68: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?

## Slide 69: ELECTRICAL HAZARDS Focus Four
Yes
Employer was operating a stand fan without grounding protection

## Slide 70: ELECTRICAL HAZARDS Focus Four
Recognize Any Hazard(s)?

## Slide 71: ELECTRICAL HAZARDS Focus Four
Yes

## Slide 72: ELECTRICAL HAZARDS Focus Four
Electrical Hazards Summary
Contact with overhead power lines causes the most electrocutions. Stay at least 10 feet away
Use GFCIs for worker protection on 120V, 15- 20-amp circuits
Make sure power is off when servicing or repairing tools and equipment
Inspect all electrical tools and cords before use.
Do not touch a worker in contact with electric current. Shut off power. If it is not possible to shut off the power, use a nonconductive material to move them or move the source of electricity.

## Slide 73: ELECTRICAL HAZARDS Focus Four
Any Questions?